Myerstown, PA  17067

October 9, 2025

Chairman Patrick Angley called the regular monthly meeting to order at 7:00 p.m., prevailing time.  The meeting was held in the Conference Room of the Myerstown Water Treatment Facility situated at 601 Stracks Dam Road, Myerstown, PA, 17067.

ROLL CALL:

Present were: Steven Hammer; Treasurer Bryan Rittle; Secretary Brian Ziegler; Vice Chairman Samuel Moyer: Chairman Patrick Angley; Engineer Farley F. Fry; Solicitor Kenneth Sandoe; and Business Manager Steven Hickernell and Operations Manager Casey Walborn.

MINUTES:

Motion by Mr. Hammer; Second by Mr. Rittle:  To approve the minutes of the September 11, 2025 meeting as distributed.  Motion passed unanimously.

CITIZEN’S COMMENTS

None

COMMUNICATIONS:

- Stoneridge set up future meeting about backflow at their facility.

- Communications were received about Well 8 and the lot off of Cherry St. with UGI.

- Cincinnati Insurance Audit was completed and a refund check of $465.00 was received for payroll audit being less than budgeted and invoiced for the year.

INVOICES:

Motion by Mr. Rittle; Second by Mr. Ziegler:  To approve payment of the invoices as presented and attached.  Motion passed unanimously.

.

FINANCIAL REPORT:

Was reviewed.

OPERATIONS REPORT FOR OCTOBER 2025:

- Continuing Bayer readings through next week. Will have a good cross section of usage through hot weather and cooler weather

- Bayer re-filled their fire tank. Slow filled through the fire line on their system. 300,000 gallons

- GAF ran fire system tests last week. 80,000 gallons. They did notify us this time of what was happening

- Filter #2 Drain/Waste valve stopped operating. I did all the troubleshooting I could. Called GES on site. Found it to be the limit switch for the opening and closing of the valve was shot. Replaced and re calibrated the opening and closing points

- Pre- Chlorine feed stopped working. Ran the feed all the way up to see if it would blow anything out. Cranked the ratio up to where we could see normal feed numbers on the rotometer and ran like that for a few hours while monitoring. Whatever was stuck in there released and the feed went back to normal. Good as of now. Hoping to avoid a service call to have them rebuild it.

- Well 6 electric repair work is complete. He did find another panel in a different box that should be replaced, it’s a cover for the bare wiring connections. New quote available. Also, while he was here, I had him look at what it would take to replace the building heater in Well 3. That will be included separately on the same quote

- Comm failure at all sites 9/30 overnight. Ryan came in and reset everything

- Checked an area on Madeliene dr. at the request of Jackson Twp. there is a section of road that appears to be “sinking”. It was repaired in 2021. We leak listened on the nearby valves as well as used the correlators. No leak found

- Followed up with PUC and notified them I would like to dispute the violation. I received an email back and they said they would reduce the fine. I declined. I’m awaiting an email back with a date for the meeting with the Damage Prevention Committee. 3-4 weeks as of 9/22/25

- VEGA rep was here to re-tune our level sensors, we were having trouble with 560 gpm mode. Should be good now. (no cost)

- Tri-annual Lead and Copper sample bottles were distributed and collected. Lead and Copper testing results received. All 20 passed. Will be sending results letters to each homeowner

| Date |  | Well #3 |  | Well #5 |  | Well #6 |  | Well #8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 9/11/2025 |  | 28' P |  | 29' S |  | 25' S |  | N/A |
| 9/18/2025 |  | 30' P |  | 37'P |  | 27' P |  | N/A |
| 9/25/2025 |  | 33'P |  | 35 ' S |  | 30' S |  | N/A |
| 10/2/2025 |  | 35' P |  | 38' S |  | 33' S |  | N/A |
| 10/9/2025 |  | 33' S |  | 43' P |  | 38' P |  | N/A |

OFFICE REPORT OCTOBER 2025

- There was 1 new connection fee paid since last meeting.

- There was 1 bad debit and 2 bad checks last month. The bad debit was for Dunkin Donuts and they had a credit, so the credit was just removed.  The 2 bad checks both paid.

- Shutoff notices were sent to 59 properties this month.

- We posted 17 properties this month.

- $25.00 credits were given to those residences that provided lead & copper samples.

- We had ordered blank bill forms about a month and a half ago and by mid September we had not received them, which was unusual.  I called our supplier and she determined that the printer was down with no estimate when it would be fixed.  She was never notified.  She found an alternative supplier that would print a slightly different bill so I only ordered 2000 instead of the usual 6000 and left the order of 6000 pending. I did not want a large amount of bills sight unseen to be printed.  She then told me they could only arrive here September 29 and our bill had to go out September 30.  We then called Coleman’s Printing and had them print, perforate, fold and insert a paper copy in a window envelope since they did not have pressure sensitive paper.  They had done this for us once before during COVID when the printer couldn’t supply us.  I now have enough bills for one more printing in November and hopefully we will get our missing order.

- Attached is a copy of the most recent Auditor’s Report that I do monthly.

CASH POSITION:

Was reviewed.

SOLICITOR’S REPORT:

Tapping fees were discussed.  Meter replacement and testing on meters 2 inches and larger were also discussed.

ENGINEER’S REPORT:

Was reviewed.

OLD BUSINESS:

The Railroad St. Project was discussed in the Engineer’s Report.

The 619-621 Railroad St. EDU and Unit update was discussed.  The owner paid the additional tapping fee of $5445.00 to increase the units by 1 from 8 to 9.

It was noted that $2000.00 was received to add to the account for the 651 W. Lincoln Ave. Escrow Account.

NEW BUSINESS:

The following motions were all made as one by Mr. Hammer; Second by Mr. Rittle:

Invoice #s 200860 for $1151.75

200865 for $880.75

200862 for $67.50

200861 for $1156.22

All to Hanover Engineering from the General Fund.  Motion passed unanimously.

The following motions were all made as one by Mr. Moyer; Second by Mr. Ziegler:

Invoice #s 200859 for $6105.92

200863 for $1926.50

200864 for $4323.36

All to Hanover Engineering from the Wilmington Trust Account.  Motion passed unanimously.

Motion by Mr. Rittle; Second by Mr. Ziegler:

Redemption 51-2024 for $15742.15

Redemption 52-2024 for $1763.40

All to A. H. Moyer from the Wilmington Trust Account.  Motion passed unanimously.

Motion by Mr. Ziegler; Second by Mr. Hammer:

Invoice #s 200866 for $1149.13

200867 for $47.25

All to Hanover Engineering from the General Account.  Motion passed unanimously.

Motion by Mr. Hammer; Second by Mr. Moyer: To purchase 500 Kamstrup meters from Core & Main at the same cost as 2025 ($315.00 per meter) for a total cost of $ 157,500.00 to be billed in 2026.  Motion passed unanimously.

Motion by Mr. Hammer; Second by Mr. Moyer: To pursue the LSA grant for the SCADA system upgrade and paving projects.  Motion passed unanimously.

EXECUTIVE SESSION

8:09 p.m. TO 8:51 p. m.

ADJOURNMENT:

No further business to come before the meeting, the meeting was adjourned at 8:52 P.M., prevailing time.

Respectfully submitted,

Brian Ziegler

Secretary

Transcribed by Terry Miller

Asst. Sec.

`